[image: image1.png]




2017-07-16

Comparison between Eco-Par® A and the requirements in the EN590 diesel fuel standard
General: Eco-Par A fulfils the ASTM D975-01 standard (grade low sulphur 2-D). Eco-Par A also fulfils the EN590 standard (arctic class 2, density: 0.80).
	Parameter
	Unit
	EN590 Requirement
	EcoPar® A Typical analysis 

	Cetane index
	-
	Min. 50
	> 60

	Cetane number
	-
	Min. 51
	51 to 54

	Density @15oC, arctic winter classes
	kg/litre
	Min. 0.80
	About 0.80

	Polycyclic aromatic hydrocarbons content
	
	Max. 8 volume%
	Below 1 ppm

	Sulphur content
	ppm wt./wt.
	Max. 10
	< 1

	Manganese content
	mg/litre
	Max 6 (after 2014)
	0

	Flash point
	oC
	Min. 55
	About 100

	Carbon residue
	wt.-%
	Max. 0.15
	< 0.1

	Ash content
	vol.-%
	Max. 0.01
	< 0.001

	Water content
	ppm wt./wt.
	Max. 200
	< 50

	Total contamination
	ppm wt./wt.
	Max. 24
	< 5

	Copper Strip Corrosion 3h at 50 oC
	
	Class 1
	Calss 1A

	Oxidation stability
	gram O2 / m3 fuel
	Max. 25
	Below 25

	Lubricity
	(m, HFRR
	Max. 400
	200 to 350

	Kinematic viscosity at 40oC
	cSt
	2.00 to 4.00
	2.7 to 3.0

	Distillation, recovered at 250 oC
	Vol%
	Max. 65
	About 50

	Distillation, recovered at 350 oC
	Vol%
	Min. 85
	Over 95

	Distillation, 95% recovered
	oC
	Max. 360
	About 340

	Fatty acid methyl ester (FAME) content
	Vol%
	Max. 7
	0.0

	Cloud point, arctic winter climates
	oC
	Max. -22
	-30 to -50, which is  lower than -22

	Cold Filter Plugging Point (CFPP)
	oC
	Max. -32 for Arctic Diesel Fuels
	-35 to -47, which is lower than -32


Note: Diesel fuels for arctic Winter climates also function in practise when it is warmer, e.g. when it is temperate Winter climates or Summer. 
Test methods used

	Parameter
	Unit
	Test method

	Flash point
	oC
	ASTM D93 or EN 22719

	Distillation, 90% recovered
	oC
	ASTM D86

	Distillation, 95% recovered
	oC
	ASTM D86 or prEN ISO 3405:1998

	Kinematic viscosity @40oC
	cSt
	ASTM D445 or EN ISO 3104

	Ash content
	vol.-%
	ASTM D482 or EN ISO 6245

	Sulphur content
	ppm wt./wt.
	EN ISO 14596:1998 or ASTM D 5453

	Copper Strip Corrosion 3h at 50 oC
	-
	ASTM D130 or EN ISO 2160

	Cetane index
	-
	ASTM D976 or EN ISO 4264

	Cetane number
	-
	ASTM D613 or EN ISO 5165:1998

	Cold Filter Plugging Point (CFPP)
	oC
	IP309 or EN116

	Cloud point
	oC
	ASTM D2500 or EN 23015

	Rams carbon residue 
	wt.-%
	ASTM D524 or EN ISO 10370

	Aromatics content
	% vol./vol.
	IP 391

	Density @15oC
	kg/litre
	ASTM D4052 or EN ISO 3675:1998

	Water content
	ppm wt./wt.
	ASTM D1744 or EN ISO 3405:1998

	Oxidation stability
	g/m3
	ASTM D2274 or EN ISO 12205

	Lubricity
	(m, HFRR
	SS-EN-ISO 12156-1

	FAME content
	Vol%
	EN14078


The chemical analyses has been performed by the international, authorized laboratory: Saybolt laboratories. Saybolt has gat laboratories for fuel analysis in many countries, e.g. UK.
Saybolt laboratories Gothenburg: 

Address: Smörjoljegatan 3
SE 418 34 Gothenburg

Sweden

Tel: +46-31-712 16 00

Fax: +46-31-54 70 99

Email: saybolt.sweden@corelab.com
Home page: http://www.corelab.com/saybolt/locations
Saybolt lab. In Gothenburg is authorized by Swedac.

Swedac´s home page:

https://www.swedac.se/?lang=en

EcoPar AB

Spadegatan 8, SE-424 65 Angered, Gothenburg, Phone: +46-31-711 50 20, Fax. +46-31-330 61 70


Organisationsnummer: 556597-9985 (Swedish Company number)

[image: image1.png]